## Annual Calc
|  | Estimated annual values based on disaggregated propane data for current campus operations | [7 empty] | Estimated Y1 Energy Costs & Electrification Savings
Building | Propane | Annual use of | Annual CO2 | Annual use of | Annual Fuel Heating | Annual Useful | Annual Useful | Electricity to Deliver | Max Rooftop Solar | Y1 Energy Cost | Y1 Energy Cost | Y1 Energy Savings | % of New Load
| Device | Propane (gal) | Emissions (kg) | Propane (kg) | Value (GJ) | Heat (GJ) | Heat (MWh) | Same Useful Heat (MWh) | Potential (MWh/y) | w/ Propane ($) | w/ HPs ($) | w/ new Tech ($) | Offset by Solar | DESCRIPTIONS
1. Administration |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
add solar PV | [8 empty] | 111 |  |  | 0 | #DIV/0! | Column C= | Average estimated annual usage in gallons, 2023-2025
2. Gym | HVAC | 2745 | 15596.5909 | 5240.4545 | 263.0708 | 210.4567 | 58.4606 | 26.573 |  | 4611.6 | 2536.395 | 2075.205 |  | Column D= | (column C)*(epa emission factor lb-CO2/gal-propane)*(unit conversion kg/lb)
add solar PV | [8 empty] | 105 |  |  | 4611.6 | 100% | Column E= | (column C)*(propane density@60F lb/gal)*(unit conversion kg/lb)
3. Community Kitchen | Stove | 34 | 193.1818 | [8 empty] | 0 |  | Column F= | (column E)*(Higher Heating Value of propane MJ/kg)*(unit conversion 0.001 GJ/MJ)
add solar PV | [8 empty] | 76 |  |  | 7015.56 | #DIV/0! | Column G= | (column F)*(typical HVAC or DHW AFUE) … use 0.8 unless you know better (boiler is 0.83)...don’t compute for stove
4. Youth Center |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Column H= | (column G)*(unit conversion MWh/GJ)
add solar PV | [8 empty] | 107 |  |  | 0 | #DIV/0! | Column I= | (column H)/(heating season <COP> or typical COP for a heat pump water heaters)
5. Natural Resources |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
add solar PV | [8 empty] | 31 |  |  | 0 | #DIV/0! | Column K= | I enters numbers from presentation
6. CFS/Police/Court | HVAC | 5609 | 31869.3182 | 10708.0909 | 537.5462 | 430.0369 | 119.4557 | 54.298 |  | 9423.12 | 5182.7466 | 4240.3734
add solar PV | [8 empty] | 101 |  |  | 9423.12 | 100% | Column M= | (column C)*(proprane price in Y1 $/gal)
7. Cultural Resources |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | Column N= | (column I)*(winter price for Schedule 24 in $/MWh)
add solar PV | [8 empty] | 27 |  |  | 0 | #DIV/0! | Column O= | (Column M)-(Column N) or Net Metered solar savings vs propane
8. Library |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
add solar PV | [8 empty] | 70 |  |  | 0 | #DIV/0! | Column P= | Percent of new load solar can offset. If 100% than there is potential to offset some existing electricity use as well.
9. Longhouse & | HVAC | 10122 | 57511.3636 | 19323.8182 | 970.0557 | 805.1462 | 223.6535 | 101.6607 |  | 17004.96 | 9703.5127 | 7301.4473
10. Education Center | [9 empty] | 0 | 0 | 0 |  | OTHER INPUT VALUES NEEDED (Check)
add solar PV | [8 empty] | 91 |  |  | 15701.6573 | 89.51% |  |  |  | 140F LWT Average COP = 2.45 kWh heat / kWh electricty
11. Elders Center | Stove | 2863 | 16267.0454 | [8 empty] | 0 |  | Heating Season Averaged ASHP <COP> |  | 2.2 | 170F LWT Average COP = 1.74 kWh heat / kWh electricty
add solar PV | [8 empty] | 79 |  |  | 7292.49 | #DIV/0! | COP for HP water heater |  | 4.5
12. Early Childhood Ed | DHW | 1058 | 6011.3636 | 2019.8182 | 101.3949 | 81.1159 | 22.5324 | 5.0072 |  | 1777.44 | 477.9367 | 1299.5033
| Stove | 2073 | 11778.4091 | [10 empty] | Propane Cost ($/gal) |  | 1.68
add solar PV | [8 empty] | 147 |  |  | 1777.44 | 100% | Electricity Cost - winter SCH 24 ($/MWh) |  | 95.45
[14 empty] | Electricity Cost - summer SCH 24 ($/MWh) |  | 92.31
SUM of Propane (gal/y) |  | 24504
Actual Annual Deliveries (2023) |  | 25784.3
Actual Annual Deliveries (2024) |  | 24201.8
Actual Annual Deliveries (2025) |  | 24852.5
Average Actual Annual Deliveries |  | 24946.2
Cleaned Annual Deliveries (2023) |  | 25345.1
Cleaned Annual Deliveries (2024) |  | 24040.5
Cleaned Annual Deliveries (2025) |  | 24139.7
Average Cleaned Annual Deliveries |  | 24508.4333
Some gallons lost from cleaning, prorating, and rounding