## Slide 1: PGST Meeting 2/6

## Slide 2: Today's Agenda
Site visit summary
Propane consumption data
ReOPT Simulation
Next steps
Final questions

## Slide 3: Site Visit
Main priorities & concerns
  Education Center & Longhouse
  Either too hot / too cold
  Malfunctions with both heating and cooling systems.
  Redundant pump systems.
  Is Elder Center included in study?

## Slide 4: Site Visit
Options for improvement
  Improve energy envelope
  Reduce redundant systems (conflicting thermostats, etc.)
    Kurt responsible for maintenance
    What is our role?
    How should we handle the uneven and inefficient HVAC system in the Education Center? By estimating the reduction in energy usage by addressing these issues?

## Slide 5: Site Visit
Where can PV be implemented?
  Longhouse not viable structurally
South facing roofs
  H, I, J, D, E
  A, B, C (future remodel)

## Slide 6: Additional Data
Post site visit Rachel sent us:
  Photos of propane appliances around complex
  Clinic microgrid performance reports
  PV data for old and new solar system
  Commercial, no-battery solar Wastewater Treatment Plant $/watt estimates
Thank you!

## Slide 7: Propane Consumption

## Slide 8: Propane Consumption

## Slide 9: Propane Consumption

## Slide 10: Propane Consumption
Key finding: Propane energy consumption was 14.7x electrical …

## Slide 11: ReOpt
We ran a ReOpt simulation based on the annual electricity and propane data:
  This software gives an estimation of how the system can be improved with the addition of PV systems.

## Slide 12: ReOpt - Assumptions
Electricity rate: PSE Inc. 24 (General Service - 3 phase)
Compensation type: Net metering (full retail rate)
Net metering system size limit: 50 kW
Compensation for excess export beyond annual purchases: $0/kWh
Existing heating system fuel type: Propane ($2.5/gal)
Analysis period: 25 years
Electricity cost escalation rate: 1.66%/year
Propane cost escalation rate: 3.48%/year

## Slide 13: ReOpt - Inputs
Office building – small
  Electricity consumption per month: Propane consumption per month:

## Slide 14: ReOpt - Findings
Reasonable PV size
  ReOpt approximates a financially optimized 45 kW PV size
Positive return on investment in the long-term
  $73,945 life cycle savings over 25 years
Reduction in grid dependence
  PV installation results in just over half the annual grid consumption (23,986 kWh compared to 44,193 kWh)
Capital cost estimates
  Total before incentives: $100,440
  About $2232/kW-DC

## Slide 15: ReOpt - Findings
PV exports and grid usage:

## Slide 16: Next Steps
Further analyze site visit information
  Examine units manufacturing plates
  Determine complex energy demand and capacity
Determine amount of heat pumps needed
  Using complex capacity data
  Offset propane usage (space heating)
Explore PV use to offset electricity usage
  Estimate capital costs and energy savings

## Slide 17: Questions
Are there any specific deliverables or deadlines you would like us to follow?
Any requests/advice in regards to the project?

## Slide 18: Thank you!