## Establish Scope of Site and Document Site Visit

- Current hydronic system configuration (temperature limitations, zones)

  - A hydronic system serves the Longhouse, with three separately thermostatted zones - each side of the bleachers and the main floor

    - The main floor is set to a constant slab temperature, heated through the main floor slab. Hydronic zones run under the bleachers.

      - On a typical 56°F day, the heating in the Longhouse keeps a 135°F cooling down temperature

      - The optimal running temperature is 195°F

      - The water loop is at a 106°F minimum high temperature

  - The Career Education Center uses an air-over-water hydraulic boiler system with redundant pumps and individual air handlers (using water to heat air and blow it into certain spots in the building).

    - Note that the boiler system operates separate from building heating in the Career Education Center because of the air-over-water component.

  - Note that no effort will be made to change the appearance of buildings (i.e., insulation).

- Which buildings are covered: site map

- Brief info on existing systems

  - Boiler-based air-over-water heating at the Career Education Center

  - Hydronic system at the Longhouse

  - Three CFS furnaces

  - Gym Furnace

  - Kitchen stoves in Kitchen, Early Childhood Center, and Elder’s center

  - Hot water heater in Early Childhood Center

- Simultaneous heating/cooling issue in Career Education Center and redundant heat pump system

  - Would be better with zone valves or dampers.

  - Inadequate integration of thermostats to control heating vs. cooling - should probably consider this when moving into electric heating scenarios.

## Document existing PV/BESS systems

- Document existing clinic solar PV system specs (kW rating, orientation)

  - 66.2 kW-DC; 60 kW-AC (which is the usable kW after conversion)

  - South facing

- Document clinic SolArk 60kW/120kWh BESS specs

  - 2 batteries at 30 kW each, 61.4 kWh each (~120 kWh total)

- Document wastewater treatment plant solar PV system specs - proposals

  - System sizes proposed were ~60-67 kW

  - Average cost per watt for proposals was ~$2.22 (per Rachel’s email):